## 📊 Dashboard
IACS CYBER SECURITY RISK REGISTER — LIVE DASHBOARD
| Document: CSMS-RA-008 ¦ Stage 2 — Risk Analysis |  |  |  | 12 May 2026
RISK POSTURE SUMMARY
| TOTAL RISKS |  | CRITICAL |  | HIGH | MEDIUM
| -483 |  | 6 |  | 0 | 0
| LOW |  | OPEN |  | IN PROGRESS | CLOSED/ACCEPT
| 0 |  | 2 |  | 4 | 0
RISK TREATMENT PROGRESS
| CRITICAL Treated |  | HIGH Treated |  | ALARP Justified | Overdue Actions
| 0% |  | N/A |  | 1 | 0
ℹ All metrics update automatically when risks are added or edited in the '📋 Risk Register' sheet. · IEC 62443-2-1:2010 §4.2 · CSMS-RA-008
Severity | Count | Status | Count | Zone | Count
CRITICAL | 6 | Open | 2 | Zone 1 (Corporate IT) | 0
HIGH | 0 | In Progress | 4 | Zone 2 (DCS/Control) | 1
MEDIUM | 0 | Closed | 0 | Zone 3 (Operations) | 1
LOW | 0 | Accepted | 0 | Zone 4 (Field/Control) | 2
|  | Deferred | 0 | Zone 5 (Safety/SIS) | 2
|  |  |  | Conduit | 0
|  |  |  | Multiple | 0

## 📋 Risk Register
IACS CYBER SECURITY RISK REGISTER · CSMS-RA-008 · Stage 2 — Risk Analysis · IEC 62443-2-1:2010 §4.2
Facility: Sunrise Refinery / Pacific Gateway Port ¦ CSMS Owner: OT Security Manager ¦ Version: 3.0 | [12 empty] | 12 May 2026
Risk ID | Scenario Description | Hazard Source | Threat Actor | Attack Vector | Zone / Conduit | Zone (Select) | CJA Target | Consequence Category | Physical Consequence | Consequence Score (C) | Existing Controls | Opportunity (1–4) | Exploitability (1–4) | Threat Capability | Reference Class | Likelihood Score (L) | Risk Score (L×C) | Risk Level (Auto) | Severity (Auto) | Evaluation Decision | Treatment Status | ALARP Justified? | Target Date | Treatment Owner | Treatment Strategy | Countermeasures | SL-T (IEC 62443) | FR Reference | Residual Score | Residual Level | Risk Acceptance By | Review Date | Notes
R-SR-001 | External attacker compromises vendor VPN (PSK, no MFA). Reaches Triconex SIS via shared DCS engineering workstation. Modifies SIS cause-and-effect matrix defeating Unit 3 ESD function. | H-SR-002: Vendor VPN PSK; H-SR-010: Flat network — SIS reachable | Organised Criminal / Nation-State | Internet → VPN → OT Network → Engineering WS → SIS | Conduit D (Vendor VPN) → Zone 2 → Zone 5 | Zone 5 (Safety/SIS) | Triconex Tricon SIS — Unit 3 ESD | Safety/HSE | ESD defeat → uncontrolled overpressure → BLEVE → Multiple fatalities | 4 | None: No MFA on VPN; No SIS network isolation; No SIS access controls | 4 | 4 | 3 | 4 | 4 | 16 | CRITICAL | CRITICAL | UNACCEPTABLE — Mandatory immediate treatment | In Progress | No | 2025-03-01 | OT Security Manager + OT Engineering | Reduce | (1) MFA on vendor VPN — FR1 SL-T3. (2) Physical SIS workstation isolation — IMMEDIATE. (3) PAM for vendor sessions — FR2 SL-T3. (4) Session recording — FR6 SL-T3. | SL-T 3 | FR1, FR2, FR6 | 8 | HIGH | Operations Director | 2025-06-01 | TRITON-class attack path. Immediate action: SIS workstation separation completed 2025-01-07. MFA in progress.
R-SR-002 | DCS compromise via IT/OT lateral movement through SCADA historian pivot. Attacker modifies process setpoints on Unit 3 high-pressure distillation column. | H-SR-001: Historian IT/OT bridge; H-SR-003: No industrial DMZ | Organised Criminal (Ransomware Adjacency) | Corporate IT → Historian bridge → DCS → Unit 3 setpoints | Zone 1 → Zone 3 (no DMZ) → Zone 2 | Zone 2 (DCS/Control) | Honeywell Experion DCS — Units 1, 2, 3 | Safety/HSE | Setpoint manipulation → reactor overpressure → VCE — potential fatalities | 4 | Historian credentials (weak); No DMZ; DCS accounts shared | 3 | 4 | 3 | 4 | 4 | 16 | CRITICAL | CRITICAL | UNACCEPTABLE — Mandatory treatment | In Progress | No | 2025-04-01 | IT Security Manager + OT Engineering | Reduce | (1) Industrial DMZ deployment — FR5 SL-T3. (2) OT-IDS Zone 3/4 — FR6 SL-T3. (3) Historian authentication — FR1 SL-T2. (4) DCS account individual — FR2 SL-T2. | SL-T 3 | FR1, FR2, FR5, FR6 | 8 | HIGH | Operations Director | 2025-06-01 | Colonial Pipeline / Oldsmar water model. Historian unauthenticated access confirmed passively (SR-PA-006).
R-SR-003 | Compressor PLCs (12 units) exploited via CVE-2022-1159 (CVSS 9.8). Attacker modifies compressor speed setpoints or disables ESD relay logic. | H-SR-005: CVE-2022-1159 applicable firmware 32.011 | Any actor with OT network access | OT network → EtherNet/IP → ControlLogix firmware exploit | Zone 4 (Control Network) — compressor subnet | Zone 4 (Field/Control) | ControlLogix PLCs — 12× compressor units | Safety/HSE | Compressor failure → hydrocarbon release → fire/explosion — CRITICAL injury risk | 3 | None: CVE unpatched 8+ months; Default credentials on some PLCs | 4 | 4 | 3 | 4 | 4 | 12 | CRITICAL | CRITICAL | UNACCEPTABLE — Emergency patch required | In Progress | No | 2025-02-15 | OT Engineering + Vendor (Rockwell) | Reduce | (1) Emergency patch CVE-2022-1159 — coordinate maintenance windows — FR3 SL-T2. (2) PLC subnet isolation — FR5 SL-T2. (3) Default credential change — FR1 SL-T2. (4) OT monitoring on PLC subnet — FR6 SL-T2. | SL-T 2 | FR1, FR3, FR5, FR6 | 3 | MEDIUM | OT Security Manager | 2025-04-01 | CISA KEV catalog entry — active exploitation confirmed in energy sector. Passive fingerprint: firmware 32.011 confirmed via enip-info.
R-SR-004 | Nation-state TRITON-class direct SIS attack. Adversary develops TriStation-aware malware to defeat Unit 3 SIS while keeping SIS apparently operational. | H-SR-010: SIS accessible from engineering network; H-SR-002: VPN path | Nation-State (XENOTIME capability) | Supply chain / engineering network → TriStation protocol → SIS | Zone 2 → Zone 5 (pre-remediation) | Zone 5 (Safety/SIS) | Triconex Tricon SIS — Unit 3 ESD | Safety/HSE | SIS defeat with concealment → process upset → BLEVE — Multiple fatalities | 4 | HIPPS (physical), PSVs (physical). No cyber controls on SIS. | 2 | 4 | 2 | 3 | 3 | 12 | CRITICAL | CRITICAL | ALARP REQUIRED — nation-state capability; all practicable controls applied | In Progress | Yes | 2025-06-01 | Process Safety Manager + OT Security Manager | Reduce | (1) SIS workstation physical isolation — DONE. (2) SIS integrity monitoring via data diode — FR6 SL-T3. (3) Two-person integrity for SIS programme changes — FR2 SL-T3. (4) Vendor access separate MFA session — FR1 SL-T3. | SL-T 3 | FR1, FR2, FR6 | 8 | HIGH | Operations Director | 2025-12-01 | ALARP case: nation-state SL-T 3+ capability. All practicable controls implemented. Post-remediation LOPA: f(consequence) = 5×10⁻⁷ ≤ CFT 10⁻⁵.
R-PGP-001 | Rogue 802.11p V2X beacon injected near terminal. IGV navigation processor accepts false position/route data. IGV directed into maintenance area — worker fatality. | H-PGP-001: V2X 802.11p — no authentication (IEEE 1609.2 WAVE Security not implemented) | Hacktivist / Insider / Organised Criminal | Wireless RF → V2X beacon injection → IGV navigation processor | Zone 4 (IGV Navigation) — V2X wireless | Zone 4 (Field/Control) | IGV Navigation System — 24 IGVs | Safety/HSE | Worker struck by 40-tonne IGV at 15 km/h — FATAL. Fleet-wide navigation corruption. | 4 | Pedestrian exclusion zone (degraded), LiDAR obstacle detection (defeatable by spoofing), hard-wired E-stop | 4 | 4 | 3 | 3 | 4 | 16 | CRITICAL | CRITICAL | UNACCEPTABLE — Mandatory treatment | Open | No | 2025-05-01 | OT Engineering + V2X Vendor | Reduce | (1) Implement IEEE 1609.2 WAVE Security (V2X authentication) — FR1 SL-T3. (2) Physical speed limiting in pedestrian zones — FR3 SL-T2. (3) MQTT TLS + HMAC — FR4 SL-T2. (4) FMS anomaly detection — FR6 SL-T2. | SL-T 3 | FR1, FR3, FR4, FR6 | 8 | HIGH | Chief Engineer — Pacific Gateway Port | 2025-06-01 | Pacific Gateway Port assessment finding T-01 (Score 16). Lab demonstration: rogue beacon accepted by test IGV navigation processor. TRITON analogy for safety system.
R-PGP-002 | MQTT broker unauthenticated. Attacker subscribes to all IGV routing topics, injects false routing commands directing multiple IGVs simultaneously. | H-PGP-002: MQTT plaintext — no TLS, no HMAC | Any actor on FMS network segment | FMS network → MQTT broker → IGV routing commands | Zone 3 (Fleet Management) → Zone 4 (IGV Navigation) | Zone 3 (Operations) | Fleet Management Server — MQTT Broker | Safety/HSE | Fleet-wide IGV navigation corruption → multiple vehicle collisions → worker fatalities / infrastructure damage | 4 | None: MQTT plaintext, no authentication, no integrity checking | 4 | 4 | 3 | 3 | 4 | 16 | CRITICAL | CRITICAL | UNACCEPTABLE — Mandatory treatment | Open | No | 2025-04-15 | IT Security Manager + FMS Vendor | Reduce | (1) MQTT over TLS (port 8883) — FR4 SL-T2. (2) HMAC message integrity on all IGV commands — FR3 SL-T2. (3) Broker authentication (client certificates) — FR1 SL-T2. (4) FMS network segmentation from TOS — FR5 SL-T2. | SL-T 2 | FR1, FR3, FR4, FR5 | 4 | MEDIUM | Chief Engineer — Pacific Gateway Port | 2025-05-01 | Active assessment finding: MQTT unauthenticated subscribe confirmed. All 24 IGV routing topics visible without credentials.

## 🎯 Risk Matrix
IEC 62443 RISK MATRIX — LIVE RISK HEAT MAP | [5 empty] | LIVE RISK COUNTS BY SEVERITY
Likelihood Score (L) × Consequence Score (C) = Risk Score · Auto-populated from Risk Register | [5 empty] | CRITICAL | 6
[6 empty] | HIGH | 0
| C=1 NEGLIGIBLE | C=2 MARGINAL | C=3 CRITICAL | C=4 CATASTROPHIC | Risk IDs in this cell | MEDIUM | 0
L=4 HIGH | [5 empty] | LOW | 0
L=3 MEDIUM-HIGH | [5 empty] | TOTAL | -485
L=2 MEDIUM-LOW
L=1 LOW
LEGEND
CRITICAL (12–16) | HIGH (6–11) | MEDIUM (3–5) | LOW (1–2)

## 🔧 Treatment Tracker
RISK TREATMENT TRACKER — Auto-linked from Risk Register · CSMS-RA-008
Risk ID | Scenario (Short) | Severity | Treatment Strategy | Treatment Owner | Target Date | Status | Days Remaining | ALARP? | Countermeasures (Summary)
R-SR-001 | External attacker compromises vendor VPN (PSK, no MFA). Reaches Triconex SIS via | CRITICAL | Reduce | OT Security Manager + OT Engineering | 2025-03-01 | In Progress | -437 | No | (1) MFA on vendor VPN — FR1 SL-T3. (2) Physical SIS workstation isolation — IMMEDIATE. (3) PAM for vendor sessions — FR2
R-SR-002 | DCS compromise via IT/OT lateral movement through SCADA historian pivot. Attacke | CRITICAL | Reduce | IT Security Manager + OT Engineering | 2025-04-01 | In Progress | -406 | No | (1) Industrial DMZ deployment — FR5 SL-T3. (2) OT-IDS Zone 3/4 — FR6 SL-T3. (3) Historian authentication — FR1 SL-T2. (4
R-SR-003 | Compressor PLCs (12 units) exploited via CVE-2022-1159 (CVSS 9.8). Attacker modi | CRITICAL | Reduce | OT Engineering + Vendor (Rockwell) | 2025-02-15 | In Progress | -451 | No | (1) Emergency patch CVE-2022-1159 — coordinate maintenance windows — FR3 SL-T2. (2) PLC subnet isolation — FR5 SL-T2. (3
R-SR-004 | Nation-state TRITON-class direct SIS attack. Adversary develops TriStation-aware | CRITICAL | Reduce | Process Safety Manager + OT Security Manager | 2025-06-01 | In Progress | -345 | Yes | (1) SIS workstation physical isolation — DONE. (2) SIS integrity monitoring via data diode — FR6 SL-T3. (3) Two-person i
R-PGP-001 | Rogue 802.11p V2X beacon injected near terminal. IGV navigation processor accept | CRITICAL | Reduce | OT Engineering + V2X Vendor | 2025-05-01 | Open | -376 | No | (1) Implement IEEE 1609.2 WAVE Security (V2X authentication) — FR1 SL-T3. (2) Physical speed limiting in pedestrian zone
R-PGP-002 | MQTT broker unauthenticated. Attacker subscribes to all IGV routing topics, inje | CRITICAL | Reduce | IT Security Manager + FMS Vendor | 2025-04-15 | Open | -392 | No | (1) MQTT over TLS (port 8883) — FR4 SL-T2. (2) HMAC message integrity on all IGV commands — FR3 SL-T2. (3) Broker authen
TREATMENT SUMMARY — auto-calculated from register above
Open | 2 | In Progress | 4 | Closed | 0 | Overdue | 6 | % Complete | 0%
Formulas:
Days Remaining = IFERROR(IF([Status]="Closed","DONE",VLOOKUP("R-SR-001",'📋 Risk Register'!A:X,24,FALSE())-TODAY()),"")
Days Remaining = IFERROR(IF([Status]="Closed","DONE",VLOOKUP("R-PGP-001",'📋 Risk Register'!A:X,24,FALSE())-TODAY()),"")

## 📖 Instructions
IACS CYBER SECURITY RISK REGISTER — USER GUIDE
HOW TO USE THIS WORKBOOK
Step 1 — Add new risks | Navigate to '📋 Risk Register'. Enter data in columns A through P (Risk ID through Reference Class). The Likelihood Score (Q), Risk Score (R), Severity (S/T), and Residual Level (AE) calculate automatically.
Step 2 — Select from dropdowns | Columns G (Zone), I (Consequence Category), M–P (Scores 1–4), V (Status), W (ALARP), Z (Strategy), AB (SL-T) all have dropdown validation. Click the cell to see the dropdown arrow.
Step 3 — Update treatment status | When you complete a countermeasure, update column V (Treatment Status) from 'Open' → 'In Progress' → 'Closed'. All dashboards update automatically.
Step 4 — Review the dashboard | The '📊 Dashboard' sheet shows live counts, KPIs, and charts. All values pull directly from the Risk Register. Refresh: press Ctrl+Alt+F9 to force recalculation.
Step 5 — Check the treatment tracker | The '🔧 Treatment Tracker' shows overdue actions (highlighted red), days remaining, and completion percentage. Update target dates in the Risk Register — the tracker updates automatically.
Step 6 — Risk Matrix | The '🎯 Risk Matrix' shows which Risk IDs sit in each cell of the IEC 62443 4×4 matrix. As you add risks, they appear automatically in the correct cell.
RISK SCORING GUIDE
Consequence Score (C) | 1 = NEGLIGIBLE (nuisance only) 2 = MARGINAL (limited production impact) 3 = CRITICAL (major operational/environmental impact) 4 = CATASTROPHIC (fatalities possible / major release)
Likelihood Inputs (1–4 each) | Opportunity: 1=Minimal, 2=Limited, 3=Significant, 4=Extensive Exploitability: 1=Very difficult, 2=Difficult, 3=Moderate, 4=Easy Threat Capability: 1=Low, 2=Medium, 3=High, 4=Very High Reference Class: 1=No precedent, 2=Rare, 3=Sector incidents, 4=Active exploitation
Risk Score = L × C | Likelihood Score = ROUND(AVG(Opp, Exploit, ThreatCap, RefClass), 0) Risk Score = Likelihood × Consequence CRITICAL: 12–16 ¦ HIGH: 6–11 ¦ MEDIUM: 3–5 ¦ LOW: 1–2
REGULATORY REFERENCES
IEC 62443-2-1:2010 §4.2 | Risk Analysis — this register is the primary output of §4.2.3 (threat and vulnerability assessment) and §4.2.3.10 (risk register maintenance SHALL requirement).
IEC 62443-2-1:2010 §4.2.3.6.5 | Risk Tolerance Criteria (SHALL): criteria must be established before the risk assessment begins. Document risk tolerance thresholds in the register header.
IEC 62443-2-1:2010 §4.2.3.13 | Risk Register (SHALL): must be maintained, reviewed at defined intervals, and updated on trigger events (architecture change, new CVE, post-incident).
ALARP (UK HSE / R2P2 2001) | Risks in the ALARP zone (HIGH) must have documented justification that all practicable controls have been implemented. Record in column W and document the ALARP case in the Notes column.
REASSESSMENT TRIGGERS
Architecture changes | Any change to OT network connectivity, new systems, or changed vendor access requires re-assessment of affected risk entries.
New vulnerability / ICS-CERT advisory | Any ICS-CERT advisory for a deployed technology requires immediate likelihood re-assessment for affected entries.
Security incident (this or peer facility) | Any OT security incident at this facility or a directly comparable facility triggers full risk register review.
Regulatory change | Any change to applicable regulatory requirements triggers compliance mapping review.
Annual review (minimum) | Complete risk register review at minimum annually. More frequent for CRITICAL risks.