## Slide 1
IEC 62443-2-1:2010
Establishing
a Cyber Security
Management
System for IACS
Complete Mastery Training
Stages 1 – 5
STAGE 1 Foundations
STAGE 2 Risk Analysis
STAGE 3 Policy & Countermeasures
STAGE 4 Implementation
STAGE 5 Monitoring & Mastery
Practical · Standards-Based · Autonomous CSMS Ready

## Slide 2
LEARNING ROADMAP
How this training is structured — 5 stages, ~52 weeks, one complete CSMS
01
FOUNDATIONS
IACS vs IT · What is a CSMS · The 3-Category Framework · Shall vs Should
Weeks 1–4
02
RISK ANALYSIS
Business Rationale · High-Level & Detailed Risk Assessment · Risk Registers
Weeks 5–10
03
POLICY, ORG & COUNTERMEASURES
Scope · Governance · Training · Network Segmentation · Access Control
Weeks 11–20
04
IMPLEMENTATION
Change Mgmt · Patch & AV · Info Classification · Incident Response
Weeks 21–32
05
MONITORING & MASTERY
Conformance Audits · KPIs · Continuous Improvement · Autonomous Operation
Weeks 33–52

## Slide 3
01
STAGE 1
Foundations
IACS vs IT Security · What is a CSMS · The 3-Category Framework
Shall vs Should · Key Terminology · Standard Architecture
IEC 62443-2-1 §0 · §1 · §2 · §3 · §4.1 · Annex B §B.1–B.3

## Slide 4
STAGE 1 · FOUNDATIONS
IACS vs IT Security — Why They Are Fundamentally Different
The same hacking technique can cause a production loss in IT but a fatality in OT
IT (Corporate Network)
Primary goal: Confidentiality
Patching: monthly cycles acceptable
Downtime: minutes — tolerable
Authentication: strict lockouts OK
Lifecycle: 3–5 years typical
Vendor independence: common
IACS / OT (Control System)
Primary goals: Safety & Availability
Patching: vendor-approved, often yearly
Downtime: unacceptable (safety risk)
Lockout: can cause HSE incident!
Lifecycle: 20–30+ years (PLCs from 1995)
Vendor lock-in: firmware dependent
⚠ KEY INSIGHT: Account lockout after failed logins — safe in IT, potentially lethal in OT. Your CSMS must never create HSE risk while reducing cyber risk.

## Slide 5
STAGE 1 · FOUNDATIONS
What is a CSMS? — The Engine Behind IACS Security
IEC 62443-2-1 §0 Introduction & §4.1 Overview
A Cyber Security Management System (CSMS) is a systematic, documented set of policies, procedures, practices, and personnel controls that protect an IACS against cyber threats — throughout its entire lifecycle.
📋 NOT a product
A CSMS is a management system — not a firewall, not a SIEM. Technology implements it; people and processes define it.
🔄 Lifecycle-based
The CSMS follows the IACS from design through commissioning, operation, and decommissioning. Risk changes; the CSMS must change too.
⚖️ Risk-driven
Every element of the CSMS traces back to an identified risk. If there is no risk, there is no requirement. Risk analysis drives all decisions.
👥 People-centred
§4.1 is explicit: most elements are 'policy, procedure, practice and personnel related.' Technology without people equals zero security.

## Slide 6
STAGE 1 · FOUNDATIONS
The 3-Category CSMS Architecture — Know This Like Your ABCs
IEC 62443-2-1 §4.1 · Figure 1 · Every requirement maps to one of these three categories
CAT 1
§4.2
Risk Analysis
Business Rationale
Risk Identification
Classification
Assessment
→
CAT 2
§4.3
Addressing Risk
with the CSMS
Security Policy, Org & Awareness
Selected Security Countermeasures
Implementation
→
CAT 3
§4.4
Monitoring &
Improving the CSMS
Conformance
Review, Improve
& Maintain
Annex B (informative) describes HOW to build the CSMS step-by-step. Clause 4 describes WHAT must be in it. Both are essential reading.

## Slide 7
STAGE 1 · FOUNDATIONS
SHALL vs SHOULD — The Most Important Reading Skill in This Standard
IEC 62443-2-1 §3.3 Conventions · This distinction determines your compliance baseline
🔴 SHALL
MANDATORY requirement.
Non-compliance = gap against the standard.
Example: 4.2.3.1 — 'The organisation SHALL select a particular risk assessment methodology.'
You MUST select and document a methodology. There is no option to skip this.
🟢 SHOULD
Strongly recommended — best practice.
Deviation must be justified.
Example: 4.2.3.2 — 'The organisation SHOULD provide participants in the risk assessment with training.'
If you skip training, you need a documented reason (e.g., all participants are already certified assessors).
🎓 Tutor Tip: Count the SHALLs in each requirement table. Those are your audit checkpoints. SHOULD items are your maturity improvement backlog.

## Slide 8
STAGE 1 · FOUNDATIONS
Annex B: Your Master Project Plan — The 6-Step CSMS Development Process
IEC 62443-2-1 Annex B (informative) · Figure B.1 · Honour the sequence — deviating causes predictable failures
1
Initiate CSMS
Program
Business rationale
+ obtain management
commitment + scope
›
2
High-Level Risk
Assessment
Identify threats,
general vulnerabilities
and consequences
›
3
Establish Policy,
Org & Awareness
Governance structure
training programme
policy suite
›
4
Detailed Risk
Assessment
Technical vulnerability
assessment per system
prioritise risk register
›
5
Select & Implement
Countermeasures
Zone segmentation
access controls
patch/AV/backup
›
6
Maintain
the CSMS
Audits, KPIs,
corrective actions
continuous improve.
⚠ Common Pitfall (Annex B warning): Jumping to detailed vulnerability assessment (Step 4) before establishing the high-level risk context (Step 2) produces technical findings that management ignores — because there is no narrative to make them meaningful.

## Slide 9
STAGE 1 · FOUNDATIONS
Key Terminology — Own This Vocabulary Before Reading Any Requirement
IEC 62443-2-1 §3.1 Terms and Definitions · These words have precise meanings in this standard
Asset
Any physical or logical object of perceived value. Includes hardware, software, data, and information.
eg: PLC, HMI application, P&ID drawing, network diagram
Risk
Likelihood that a threat exploits a vulnerability × the consequence of that event occurring.
eg: P = Moderate, C = Catastrophic → High Risk requiring immediate countermeasure
Security Zone
A logical or physical grouping of IACS assets sharing common security requirements and a target security level.
eg: Control Network Zone, DMZ, Corporate Zone — each with its own SL-T
Target Security Level (SL-T)
The desired security level for a zone, determined by risk assessment. Drives all countermeasure selection.
eg: SL-T 2 for a water treatment plant control zone — 'protection against intentional violation'
Conformance
The state of adhering to stated CSMS policies and executing procedures at the correct time.
eg: If your policy says 'patch within 30 days', but patches are applied at 90 days — non-conformance.
HSE
Health, Safety and Environment — always evaluated alongside cyber security decisions in IACS contexts.
eg: A patch causing a PLC reboot during production = unacceptable HSE risk → defer, test in staging

## Slide 10
02
STAGE 2
Risk Analysis
Business Rationale · High-Level Risk Assessment · Detailed Vulnerability Assessment
Risk Registers · Reassessment Triggers · Practical Worked Example
IEC 62443-2-1 §4.2 · Annex A §A.2 · Annex B §B.3–B.4 · Tables A.1–A.6

## Slide 11
STAGE 2 · RISK ANALYSIS
Element: Business Rationale — Securing Management Commitment First
§4.2.2 · Annex B Step 1 · Without this, your CSMS will be defunded when priorities shift
SHOULD
4.2.2.1 — The organisation SHOULD develop a high-level business rationale for the CSMS based on the organisation's specific cyber risk, safety requirements, and regulatory obligations.
✏ Practical Example: Business Rationale for Sunrise Refinery CSMS
💰 Business Driver
Sunrise Refinery processes 120,000 bbl/day. A cyber incident disabling the DCS for 48h = $14.4M lost production + regulatory penalties.
🛡️ Safety Driver
A Triconex SIS on Unit 3 was discovered connected to the corporate LAN. An adversary with access could disable emergency shutdown. HSE risk: catastrophic.
⚖️ Regulatory Driver
NERC CIP (if grid-connected), NIST CSF, and local HSE regulator are requiring documented CSMS by Q3. Non-compliance = operating licence risk.
👥 Stakeholder Alignment
Operations, Maintenance, IT, and Safety — all identified as co-owners. CSMS Steering Committee established reporting to Plant Manager.

## Slide 12
STAGE 2 · RISK ANALYSIS
Selecting Your Risk Assessment Methodology — A SHALL Requirement
§4.2.3.1 (SHALL) · §4.2.3.2 (SHOULD) · You must choose, document, and train on your method
SHALL
4.2.3.1 — The organisation SHALL select a particular risk assessment methodology.
HAZOP / LOPA
Best fit: Process industries (refinery, chemical, oil & gas)
✅ Integrates with existing process safety. Team familiar with it.
⚠ Can be slow; needs process knowledge. Not cyber-native.
ISA/IEC 62443
Risk Matrix
Best fit: Purpose-built for IACS environments
✅ Directly aligned to this standard. SL-T output. Industry accepted.
⚠ Requires OT + cyber expertise in the assessment team.
NIST SP 800-30
Best fit: Organisations with existing IT risk programmes
✅ Well documented. Connects IT and OT risk. Widely understood.
⚠ Not OT-native — needs adaptation for real-time IACS constraints.
Bow-Tie Analysis
Best fit: High-consequence facilities (nuclear, water, power)
✅ Visual; shows barriers clearly. Regulator-friendly. HSE integrated.
⚠ Resource-intensive. Complex for large IACS inventories.
🎓 Tutor note: Document WHY you chose this methodology. The standard requires you to have selected it — an external auditor will ask to see the documented selection and the team training records.

## Slide 13
STAGE 2 · RISK ANALYSIS
Practical: Build Your Risk Matrix — Likelihood × Consequence
Annex A Tables A.1, A.2, A.3 · The foundation of every risk scoring decision
LIKELIHOOD SCALE (Table A.1)
High
(4)
Likely to occur in the next 12 months
eg: Unpatched HMI with internet exposure
Medium
(3)
Could occur within 5 years
eg: Phishing email targeting control room operator
Low
(2)
Unlikely — requires specific knowledge
eg: Nation-state targeting obscure legacy PLC
Remote
(1)
Only with exceptional circumstances
eg: Air-gapped SIS in locked room
CONSEQUENCE SCALE (Table A.2)
Catastrophic
(4)
Fatalities, major environmental damage, total production loss
Critical
(3)
Serious injuries, significant environmental impact, months offline
Marginal
(2)
Minor injuries, limited env. impact, days offline, recoverable
Negligible
(1)
No injury, no env. impact, hours offline, fully recoverable
Risk Level = Likelihood (1–4) × Consequence (1–4). Next slide shows the full risk matrix and how to score your IACS assets.

## Slide 14
STAGE 2 · RISK ANALYSIS
Practical: Scoring the Risk Register — Sunrise Refinery Example
Annex A Tables A.3, A.5, A.6 · §4.2.3.13 (SHALL document results) · This is your living risk management document
RISK MATRIX (Likelihood × Consequence)
↑ Likelihood
Consequence →
Neg(1)
Marg(2)
Crit(3)
Catas(4)
Remote(1)
Low(2)
Medium(3)
High(4)
LOW
MED
HIGH
HIGH
LOW
MED
HIGH
HIGH
MED
HIGH
HIGH
CRIT
HIGH
HIGH
CRIT
CRIT
RISK REGISTER EXTRACT — Sunrise Refinery (§4.2.3.13 SHALL)
Asset
Threat Scenario
L
C
Risk
Required Action
Unit 3 DCS (Triconex)
LAN-connected SIS reachable from corporate
3
4
CRIT
Immediate isolation — air gap
Control Room HMI
Unpatched Windows 7, no AV, USB enabled
4
3
CRIT
Patch/replace; disable USB
SCADA Historian
Accessible from DMZ without authentication
3
3
HIGH
Auth required; VLAN isolation
Pipeline Compressor PLC
Default vendor password unchanged
4
2
HIGH
Change passwords immediately
Field Instruments
No cyber interface — physical tamper only
1
3
LOW
Physical perimeter control

## Slide 15
STAGE 2 · RISK ANALYSIS
Reassessment Triggers — When Must You Re-Run the Risk Assessment?
§4.2.3.10 (SHALL) · §4.2.3.12 (SHALL across all lifecycle stages) · Risk is not static
SHALL
4.2.3.10 — The organisation SHALL identify the risk and vulnerability reassessment triggers — events that require a new assessment.
🔧 Major IACS Change
› New PLC/DCS system installed in a zone
› SCADA software version upgrade
› Network architecture change — new DMZ created
› Integration of new vendor system
🚨 Security Incident
› Malware detected on OT network
› Unauthorised access to control system
› Near-miss: USB found in control room
› Ransomware hit a peer company in same industry
🌐 External Change
› New published vulnerability in your PLC firmware
› Regulator issues new cyber security guidance
› Threat landscape change — new ICS-CERT advisory
› Supplier security breach impacting your systems
⏰ Elapsed Time
› Minimum: annual full review of risk register
› High-risk zones: 6-monthly lightweight review
› Post-commissioning review at 12 months
› Contract renewal with vendors accessing IACS
🎓 §4.2.3.12 (SHALL): Risk assessments must be conducted through ALL stages of the IACS lifecycle — design, commissioning, operation, and decommissioning. Add this to your project gate reviews.

## Slide 16
03
STAGE 3
Addressing Risk
with the CSMS
CSMS Scope & Governance · Training Programme · Security Policies
Network Segmentation · Access Control (3 elements) · Physical Security · Personnel Security
IEC 62443-2-1 §4.3.1–4.3.3 · Annex A §A.3.2–A.3.3 · Annex B §B.5–B.6

## Slide 17
STAGE 3 · POLICY & CONTROLS
Element: CSMS Scope — Define Before You Build Anything Else
§4.3.2.2 · 4.3.2.2.1 SHALL · 4.3.2.2.2 SHOULD · The scope is your CSMS charter — everything flows from it
SHALL
4.3.2.2.1 — The organisation SHALL develop a formal written scope for the cyber security programme.
✏ Practical Example: CSMS Scope Statement — Sunrise Refinery
CSMS SCOPE DOCUMENT v1.0 | Sunrise Refinery | Approved: Plant Manager | Date: 2024-Q1
Included Systems:
DCS (Units 1–3), SCADA Historian, HMIs (Control Room + Field), Tank Farm PLC, Compressor PLC, Fire & Gas System (read-only monitoring interface)
Excluded Systems:
Corporate ERP (SAP) — covered by separate IT ISMS. Laboratory LIMS — assessed as low risk, added in Phase 2 scope expansion.
Included Locations:
Main plant (Process Areas 1–4), Control Building, Offsite Pump Station #2 (remote SCADA link)
Strategic Goals:
Achieve and maintain SL-T 2 for all control zones. Integrate with existing HSE management system. Comply with regulatory framework by Q3.
Timing:
Phase 1 (Months 1–6): Risk assessment + policy. Phase 2 (Months 7–12): Countermeasures. Phase 3 (Month 13+): Sustain & audit.
🎓 The scope SHOULD explain strategic goals, process, and timing (4.3.2.2.2). A narrow initial scope with planned expansion is better than an overambitious scope that stalls.

## Slide 18
STAGE 3 · POLICY & CONTROLS
Element: Security Policies & Procedures — The Written Rules of Engagement
§4.3.2.6 · 6 SHALL requirements · Policies are the CSMS skeleton — procedures are the muscle
POLICY HIERARCHY
Level 1: Corporate Security Policy
High-level commitment. Signed by CEO/Plant Mgr. Sets risk tolerance. 1 page.
Level 2: IACS Cyber Security Policies
Topic policies: Access Control, Change Management, Patching, Incident Response. 5–15 pages each.
Level 3: Procedures & Work Instructions
Step-by-step: 'How to request access', 'How to apply a patch'. Operators follow these.
Level 4: Records & Evidence
Completed forms, audit logs, training records, incident reports. These prove compliance.
KEY SHALL REQUIREMENTS (Table 7)
SHALL
4.3.2.6.1
Develop high-level IACS cyber security policies approved by management
SHALL
4.3.2.6.2
Develop approved cyber security procedures based on the policies
SHALL
4.3.2.6.4
Policies and procedures SHALL include compliance requirements
SHALL
4.3.2.6.5
Determine and document the organisation's risk tolerance
SHALL
4.3.2.6.6
Communicate policies and procedures to all appropriate personnel
SHALL
4.3.2.6.7
Review and update regularly — validate they are current and followed
SHALL
4.3.2.6.8
Senior leadership SHALL endorse cyber security policies visibly

## Slide 19
STAGE 3 · POLICY & CONTROLS
Element: Network Segmentation — Zones, Barriers & the Purdue Model
§4.3.3.4 · All 3 requirements are SHALL · Figures A.8 & A.9 reference architecture
SHALL
4.3.3.4.1 — Develop zone-based segmentation architecture for IACS devices based on risk level.
SHALL
4.3.3.4.2 — High-risk IACS SHALL be isolated or use barrier devices.
SHALL
4.3.3.4.3 — Barrier devices SHALL block ALL non-essential traffic in/out of critical zones.
✏ Sunrise Refinery Zone Architecture
CORPORATE ZONE (L4)
ERP, Email, SharePoint | Risk: Medium | SL-T: 1
🔥 FIREWALL / DMZ
DMZ (SUPERVISORY L3)
Historian, Jump Server, Patch Server | Risk: High | SL-T: 2
🔥 FIREWALL (OWF rule set)
CONTROL ZONE (L2) — CRITICAL
DCS, HMIs, PLC Network | Risk: CRITICAL | SL-T: 2–3
SAFETY ZONE (SIS — AIR GAPPED)
Triconex SIS — Unit 3 | No network connection | Physical only access
Key Design Rules:
Traffic flows downward only — never permit unsolicited inbound from corporate to control zone
Barrier devices block ALL non-essential ports — whitelist approach, not blacklist
Jump server in DMZ for vendor remote access — never direct connection to control zone
Unit 3 SIS: physically air-gapped after risk assessment identified critical exposure
Wireless: prohibited in control zone — any exception requires risk assessment approval

## Slide 20
STAGE 3 · POLICY & CONTROLS
Access Control — Three Interlocking Elements (Must Work Together)
§4.3.3.5 Account Admin · §4.3.3.6 Authentication · §4.3.3.7 Authorization · All three SHALL requirements
👤 Account Administration
§4.3.3.5
Access granted/changed/removed by authorised manager only (4.3.3.5.3)
Record ALL accounts with names + permissions (4.3.3.5.4)
Remove/suspend unneeded accounts immediately (4.3.3.5.5)
Change default passwords before service (4.3.3.5.7)
eg:
Sunrise Refinery: After contractor completes annual outage, IT has 24h SLA to disable their accounts. Accounts reviewed quarterly. Spreadsheet of all IACS accounts maintained by OT Lead.
🔐 Authentication
§4.3.3.6
Authenticate ALL users before system use (4.3.3.6.2)
Strong auth (complex passwords) on all admin accounts (4.3.3.6.3)
Authenticate remote users at appropriate strength (4.3.3.6.5)
Develop remote login policy with failed-attempt response (4.3.3.6.6)
eg:
OT-specific caution: Account lockout after 5 failed attempts — but OWS consoles running batch processes: operators must be able to unlock immediately. Physical presence in control room = compensating control for some systems.
🔑 Authorization
§4.3.3.7
Define authorization security policy with documented role-based rules (4.3.3.7.1)
Combine logical AND physical permission methods (4.3.3.7.2)
eg:
Role table: Operator = read + setpoint only. Engineer = read + configure. Admin = full. No single role has permission to both approve and implement a change (separation of duties). Safety implications reviewed for all roles.

## Slide 21
STAGE 3 · POLICY & CONTROLS
Element: Staff Training & Security Awareness — A SHALL Programme
§4.3.2.4 · Table 5 · 6 requirements · A policy no one knows is a policy that doesn't exist
SHALL
4.3.2.4.1 — SHALL design and implement a cyber security training programme. 4.3.2.4.2 — ALL personnel SHALL receive procedure and security training.
✏ Sunrise Refinery Training Matrix
Role / Module
Cyber Awareness (1h)
CSMS Overview (2h)
Safe USB Policy (0.5h)
Incident Reporting (1h)
OT-specific Threats (3h)
Change Mgmt Procedure (2h)
All Staff
✓
✓
✓
Control Room Operators
✓
✓
✓
✓
✓
OT Engineers
✓
✓
✓
✓
✓
✓
IT / Network Team
✓
✓
✓
✓
✓
3rd Party Contractors
✓
✓
✓
Management / Steering
✓
✓
SHALL also: validate training on-going (4.3.2.4.4 SHOULD) · revise as required (4.3.2.4.5 SHALL) · maintain employee training records and schedules (4.3.2.4.6 SHOULD)

## Slide 22
04
STAGE 4
CSMS Implementation
Change Management · Patch Management · Antivirus/Malware · Backup & Recovery
Information Classification · Incident Response (3 Phases) · Drills & Exercises
IEC 62443-2-1 §4.3.4 · Annex A §A.3.4 · Annex B §B.7

## Slide 23
STAGE 4 · IMPLEMENTATION
Element: Change Management — Separation of Duties is Non-Negotiable
§4.3.4.3.2 SHALL · §4.3.4.3.3 SHALL · Same person cannot BOTH approve AND implement a change
SHALL
4.3.4.3.2 — A change management system SHALL be developed with separation of duty principles — the same individual cannot approve and implement a change.
✏ Sunrise Refinery: OT Change Management Workflow
1
Requester
(Operator / Engr)
Raise RFC
(Request for Change)
›
2
OT Security
Advisor
Cyber + HSE
Impact Assessment
›
3
Change Advisory
Board (CAB)
Review & Approve
or Reject
›
4
OT Engineer
(NOT requester)
Implement in
Staging/Test first
›
5
Independent
Verifier
Test & Verify
in Test Env.
›
6
CAB / OT Lead
Approve for
Production Deploy
›
7
OT Engineer
Deploy + Record
in Change Log
⚠ OT-Specific: §4.3.4.3.3 (SHALL) requires technically knowledgeable review of HSE and cyber security risk for ALL proposed changes. Include process safety engineers in the CAB for IACS changes.

## Slide 24
STAGE 4 · IMPLEMENTATION
Element: Patch Management — OT Patching is NOT the Same as IT Patching
§4.3.4.3.7 SHALL · Annex A §A.3.4.3.7 · Must determine risk of applying AND not applying
SHALL
4.3.4.3.7 — A procedure for patch management SHALL be established, documented, and followed.
✏ OT Patch Decision Framework — Annex A §A.3.4.3.7
1. IDENTIFY
Subscribe to ICS-CERT, vendor security advisories.
Receive notification: Rockwell Allen-Bradley PLC vulnerability CVE-2024-XXXX.
2. ASSESS RELEVANCE
Is my firmware version affected? Is this PLC in my scope?
Result: YES — Unit 1 DCS PLC running v2.4 (affected). Unit 2: v2.6 (not affected).
3. RISK IF APPLIED
Patch requires PLC restart (3–5 min downtime). Impact on SL-T?
Unit 1 scheduled maintenance in 6 weeks — target patch during planned outage.
4. RISK IF NOT APPLIED
CVE allows remote code execution via Ethernet. CVSS: 9.8.
Unit 1 in control zone — high consequence if exploited. Risk: CRITICAL. Compensating control: isolate from network until patched.
5. TEST → DEPLOY
Deploy patch to identical staging PLC. Run for 72h. Test all control functions. Vendor sign-off obtained. Deploy during outage. Update asset register.
🎓 Never patch an OT system in production without testing in staging first (Annex A §A.3.4.3.5.6 — baseline practice). Never reuse the IT patch calendar for OT — coordinate with vendor and operations.

## Slide 25
STAGE 4 · IMPLEMENTATION
Element: Incident Planning & Response — Predefined Before the Crisis Hits
§4.3.4.5 · Table 17 · 3 Phases: Plan → Respond → Recover · §4.3.4.5.1 SHALL
SHALL
4.3.4.5.1 — SHALL implement an incident response plan identifying responsible personnel and defining actions.
📋 PHASE 1: PLAN
Write IRP — name responsible personnel (SHALL)
Define incident categories: malware, DoS, intrusion, accidental
Establish unusual-activity reporting procedure (SHOULD)
Obtain stakeholder sign-off: Ops, IT, Safety, Management
Test with regular drills (SHOULD) — document outcomes
eg: Sunrise IRP defines: Security Lead = OT Manager. Backup = HSE Manager. Contact list laminated in control room. Escalation matrix for each incident type posted on wall.
🚨 PHASE 2: RESPOND
Detect and classify: Is it a cyber incident?
Execute IRP — follow procedure (do NOT improvise)
Contain: isolate affected system from network
Preserve evidence where possible
Communicate to all appropriate organisations (SHALL)
Document EVERYTHING in real time (SHALL 4.3.4.5.8)
eg: Key tension: forensics vs. production recovery. Decide IN ADVANCE which takes priority for each system. Unit 1 DCS = get running fast. Corporate network = preserve forensics.
🔄 PHASE 3: RECOVER
Restore from validated, tested backups
Run system tests before returning to production
Identify root cause — document in incident report
Communicate findings to all affected parties
Address and correct issues found (SHALL 4.3.4.5.10)
Update CSMS policies/procedures based on lessons learned
eg: Post-incident review within 5 working days. Findings fed back into risk register. CSMS updated if gap identified. Management briefed with incident summary report.

## Slide 26
STAGE 4 · IMPLEMENTATION
Element: Information Classification — CSMS Documents Are Sensitive Assets
§4.3.4.4 · 4.3.4.4.1 SHALL · 4.3.4.4.2 SHALL · Your vulnerability assessment is more dangerous in the wrong hands than a key
SHALL
4.3.4.4.3 (SHALL) — All logical assets within the scope of the CSMS SHALL be classified to indicate the protection required commensurate with the consequence of unauthorised disclosure.
RESTRICTED
Examples: Vulnerability assessment results · Network architecture diagrams (detailed) · Risk register with asset details · CSMS policies and procedures · IRP with contact names
Handling: Need-to-know: CSMS team only. Encrypted storage. No email without encryption. Shred physical copies. Never in cloud without approval.
CONFIDENTIAL
Examples: IACS inventory (high-level) · Incident investigation reports · Audit findings · Patch schedule · Training records
Handling: Internal staff only. Password-protected files. Access controlled by OT Manager. Log who accesses these documents.
INTERNAL
Examples: General security awareness materials · Emergency contact lists · Site maps (non-detailed) · Approved vendor lists · Training schedules
Handling: All employees. Normal access controls apply. Do not share externally without approval.
PUBLIC
Examples: General company information · Regulatory filing summaries (public) · Emergency contact for public (non-specific)
Handling: No restrictions. Can be shared externally freely.

## Slide 27
05
STAGE 5
Monitoring &
Mastery
Conformance Audits · KPIs · The 5-Step CSMS Change Process
Continuous Improvement · Autonomous CSMS Operation
IEC 62443-2-1 §4.4 · Annex A §A.4 · Annex B §B.8

## Slide 28
STAGE 5 · MONITORING & MASTERY
Element: Conformance — Validating the CSMS is Actually Used
§4.4.2 · Table 18 · §4.4.2 Rationale: 'If it is not used, it does not add any value'
"Irrespective of the quality of a CSMS, if it is not used, it does not add any value and does not help reduce risk." — IEC 62443-2-1 §4.4.2 Rationale
✏ Sunrise Refinery Conformance Audit Programme (4.4.2.1 SHALL)
Quarterly Spot Check
Scope: Account review: all IACS accounts vs. active employees. Default passwords. Terminated user cleanup.
Evidence: Account audit report, exception log, remediation tracker.
Method: OT Security Lead reviews AD/account lists. Compare vs. HR changes in quarter.
Bi-Annual Technical
Scope: Firewall rules vs. approved whitelist. Patch status vs. schedule. AV signatures. Backup test result.
Evidence: Firewall rule review report. Patch compliance %. Backup verification log.
Method: OT Engineer + external specialist. No disruption to production — read-only review.
Annual Full CSMS Audit
Scope: All 19 requirement tables from Clause 4. Policy currency. Training records. Incident register review.
Evidence: Full audit report with KPI results. Non-conformances listed. Management presentation.
Method: Cross-functional team: OT, IT, HSE, Management. One Clause 4 section per week over 4 weeks.
Unscheduled (Triggered)
Scope: Any element affected by the triggering event (incident, major change, regulatory update).
Evidence: Trigger event log. Impact assessment. CSMS update record if required.
Method: Immediate review by CSMS owner. Determine scope of CSMS impact within 48h.
Also SHALL: Define punitive measures for non-conformance (4.4.2.5) · Specify auditor competency (4.4.2.6 SHOULD) · Maintain document audit trail (4.4.2.4 SHALL)

## Slide 29
STAGE 5 · MONITORING & MASTERY
KPI Programme — Measuring What Matters for Autonomous CSMS Operation
Annex A §A.4.2.3 · 7-Step Metrics Programme · Quantitative KPIs that create automatic accountability
WATCH
Patch Compliance Rate
94%
↑
Target: ≥95%
Patches applied within SLA
ON TARGET
Open Audit NCs
3
↓
Target: <5
Non-conformances open
ON TARGET
Account Review Compliance
100%
→
Target: 100%
Quarterly reviews completed
AT RISK
Incident Drill Frequency
2/yr
↑
Target: 4/yr
Tabletop exercises held
ON TARGET
Mean Time to Patch (Critical)
22d
↓
Target: ≤30d
Avg days to apply critical patch
WATCH
Staff Training Completion
87%
↑
Target: 100%
Role-mandatory training done
🎓 Report KPIs to management quarterly. Poor marks over two consecutive periods = systemic problem requiring root cause analysis. Define thresholds that trigger unscheduled CSMS review (§4.4.3.3 SHOULD).

## Slide 30
STAGE 5 · MONITORING & MASTERY
The 5-Step CSMS Change Management Process — Keeping the CSMS Current
Annex A §A.4.3.5 · §4.4.3.1 SHALL assign an organisation to manage CSMS changes
SHALL
4.4.3.1 — An organisation SHALL be assigned to manage and coordinate CSMS refinement and changes using a defined method.
1
Define Current CSMS
Document everything: all policies, assets, procedures related to the CSMS. All stakeholders must understand the baseline before proposing changes.
eg: Before proposing any change, OT Manager distributes current policy list and asset inventory to CAB. Version numbers confirmed.
2
Identify Gaps & Weaknesses
Review for compliance + effectiveness. Identify gaps against the standard. Consider industry best practices (§4.4.3.6 SHOULD: monitor industry CSMS strategies).
eg: Annual audit found: no formal vendor management procedure. ICS-CERT advisory highlighted new threat vector not in risk register.
3
Propose & Evaluate Changes
Document changes concisely. Present to stakeholders. Evaluate for side effects. Validate new technology before incorporating — especially critical in OT.
eg: Proposed: add vendor remote access procedure. Evaluated: impact on firewall rules, jump server capacity, SIS air gap integrity. No negative side effects found.
4
Implement Changes
Follow company procedures. Obtain written approval from key stakeholders. Special attention to systems testing, validation, and vendor involvement for technical changes.
eg: Policy approved by Plant Manager. OT Engineer implements jump server configuration. IT verifies firewall rules. CAB signs off. Policy issued to all staff.
5
Monitor Performance
With new/revised CSMS in place, monitor and evaluate its performance. Conduct review on a regular basis and whenever further changes occur.
eg: New vendor procedure: 90-day review scheduled. Track: vendor access requests, connection duration, any anomalies. Incorporate into next quarterly audit.

## Slide 31
STAGE 5 · MONITORING & MASTERY
CSMS Review Triggers — What Forces a Review Without Being Asked?
§4.4.3.3 SHOULD · Minimum triggers: serious incidents, legal/regulatory changes, risk changes, major IACS changes
Establishing triggers makes the CSMS self-correcting — the system tells you when to review, rather than relying on memory.
✏ Sunrise Refinery: CSMS Review Trigger Register (§4.4.3.3)
Trigger
Threshold
Required Action
Security Incident — Severity HIGH/CRITICAL
Any incident classified as High or Critical on Sunrise severity matrix
Full CSMS review within 30 days. Update risk register and IRP.
Regulatory Change
New or amended OT cyber security regulation from NIST, IEC, or national regulator
Compliance gap analysis within 60 days. CSMS update if required.
Major IACS Change
Addition, replacement, or major upgrade of any SL-T≥2 asset
Zone-specific risk reassessment before commissioning. Update asset inventory.
KPI Consecutive Failure
Same KPI below target for 2 consecutive reporting periods
Root cause analysis within 30 days. Corrective action plan with owner and due date.
Industry Threat Alert
ICS-CERT advisory with CVSS ≥ 8.0 affecting assets in our inventory
Immediate technical review. Compensating controls if patch unavailable.
Elapsed Time
12 months since last full CSMS review (regardless of other triggers)
Annual full CSMS review per audit programme.

## Slide 32
STAGE 5 · MONITORING & MASTERY
Mastery Checklist — How to Know Your CSMS is Truly Autonomous
All 5 stages complete · An autonomous CSMS finds its own weaknesses, fixes them, and proves it
1
Can draw the 3-category CSMS architecture and map any control to its category
2
A complete, management-signed risk register exists with prioritised risks and owners
2
Reassessment triggers documented and tested — risk assessment repeated at least once
3
Policy suite written, management-endorsed, communicated, reviewed within last 12 months
3
Network zone architecture implemented and verified with firewall rule review
3
Training completion records exist for all in-scope personnel
4
Change management system operating with documented separation of duties for all changes
4
At least one full incident response drill completed and debriefed
4
Backup restoration tested — successfully recovered test system from backup
5
KPI dashboard reported to management quarterly — at least one full cycle completed
5
At least one non-conformance identified, documented, and resolved through formal process
5
CSMS updated at least once based on audit findings, incident, or trigger event

## Slide 33
CONGRATULATIONS
You Have Completed the IEC 62443-2-1
CSMS Mastery Programme
1
Compliant
You have all SHALL requirements documented, approved, and implemented. An external auditor would find no major gaps. The CSMS exists.
2
Effective
Your CSMS demonstrably reduces risk. Incidents are detected, responded to, and learned from. KPIs show improving trend. The CSMS works.
3
Autonomous
The CSMS finds its own weaknesses through triggers and audits. It updates itself through the 5-step process. It requires no external prompting. The CSMS is institutionalised.
IEC 62443-2-1:2010 · Complete Training Deck · Stages 1–5 · Practical & Standards-Based