## Slide 1
IEC 62443-2-1:2010
OT Risk Assessment
Methodologies
Complete Training Programme
Stages 1 – 5
01
STAGE 01
OT vs IT Risk Fundamentals
02
STAGE 02
The 5 Methodologies
03
STAGE 03
The Decision Matrix
04
STAGE 04
Worked Examples
05
STAGE 05
Application & Mastery
For IT Risk Professionals entering OT Security

## Slide 2
01
STAGE 1
OT vs IT Risk
Fundamentals
Why your IT risk toolkit will fail — and sometimes harm — when applied to IACS without adaptation
IEC 62443-2-1:2010 · §4.2 · §4.2.3.1 SHALL

## Slide 3
STAGE 1 · FOUNDATIONS
Why OT Risk Assessment is Fundamentally Different
The same cyber incident that causes a data breach in IT causes a physical catastrophe in OT
Dimension
IT Security
OT / IACS Security
Primary goal
Confidentiality of data
Safety, availability, process integrity
Worst case
Data breach, reputation loss, fines
Personnel fatality, environmental release
Downtime tolerance
Hours — BCP acceptable
Often ZERO — shutdown itself creates HSE risk
Patch cadence
Monthly Patch Tuesday — routine
Vendor-coordinated, outage-window, often annual
Account lockout
Safe — standard security practice
CAN BE LETHAL — HMI lockout during emergency
CAN BE LETHAL — HMI lockout during emergency
Active vuln scan
Routine — run continuously
Can CRASH PLCs — requires vendor approval
Can CRASH PLCs — requires vendor approval
System lifetime
3–5 years — planned refresh
20–30+ years — 1990s PLCs still in service
KEY INSIGHT
§4.2.3.11 (SHALL): Physical, HSE, and cyber security risk results MUST be integrated. A control that creates a new safety hazard is not a security improvement.
§4.2 · The IT risk toolkit you know was built for a world where the worst outcome is information loss. In OT, the worst outcome is physical.

## Slide 4
STAGE 1 · FOUNDATIONS
Three Interlocking Risk Domains — No Single IT Method Covers All Three
🔒
Cyber Domain
Attack paths, threat actors, vulnerability exploitation, network exposure, authentication gaps.
This is where IT risk tools have the most applicability — but they still need OT context.
⚠
Physical / Safety Domain
What happens physically when a cyber attack succeeds.
A manipulated PLC setpoint is NOT a data integrity issue. It is a vessel overpressure, a hoist collision, a gas release. The consequence chain is physical.
🔄
Operational Domain
Production continuity, process integrity, and the risks created BY security controls.
An access lockout preventing an operator from responding to an alarm creates a new, greater risk than the one being mitigated.
▶
▶
Effective OT risk assessment requires a hybrid approach — because no single methodology addresses all three domains simultaneously.

## Slide 5
STAGE 1 · PRACTICAL EXAMPLE
Practical: Applying ISO 27005 to a DCS — Where It Breaks Down
Sunrise Refinery · Unit 3 DCS Pressure Controller · Step-by-step failure analysis
1
Asset Identification
IT approach: DCS controller listed as an asset ✓
OT problem: PLC control logic and setpoint tables are listed as 'data'. Problem: losing their integrity is not a data issue — it is a process safety case failure. ISO 27005 has no framework for this.
2
Threat Identification
IT approach: Threat library includes malware, DoS, credential theft
OT problem: Primary DCS threats are MISSING: process manipulation (setpoint to 200% of safe level), safety system defeat (interlock disable), denial of view (HMI alarm flooding). Not in any IT threat library.
3
Impact Assessment
IT approach: Financial loss, reputation, regulatory penalty scored
OT problem: Safety consequence is entirely absent from the scoring framework. A DCS cyber incident causing a fatality scores the SAME as a data breach costing the same financial amount. Risk is systematically underestimated.
4
Control Selection
IT approach: Controls from ISO 27001 Annex A selected
OT problem: Mandatory password complexity → operators cannot log in during emergency. Automated session timeout → critical HMI screens go dark. The controls create new hazards by design.
The direction of analysis is reversed in OT: start with physical consequence, work backwards to cyber threats. Not vulnerability → impact.

## Slide 6
STAGE 1 · §4.2 SEQUENCE
The IEC 62443-2-1 Risk Model — A Specific Sequence You Must Follow
1
High-level risk assessment FIRST
§4.2.3.3 SHALL
Characterise threats, general vulnerabilities, consequences at the system level. This is the risk narrative management needs BEFORE seeing technical findings. Skipping this produces ignored reports.
2
System prioritisation
§4.2.3.6 SHALL
Rank IACS systems by risk. Detailed assessment resources go to P1 systems first. Document criteria — safety consequence × connectivity × existing controls.
3
Detailed vulnerability assessment
§4.2.3.7 SHALL
Technical assessment of specific exploitable weaknesses on P1/P2 systems. ICS-specific expertise required. Active scanning may crash PLCs — requires vendor approval and change management.
4
Detailed risk assessment (selected methodology)
§4.2.3.9 SHALL
Apply your documented methodology. Score every risk. Feed results into the Risk Register (CSMS-RA-008). Every risk traces to threat + vulnerability + consequence.
Annex B, Step 2 is explicit: do NOT jump to detailed vulnerability assessment before the high-level risk assessment is complete. Detailed findings without risk narrative = ignored reports.

## Slide 7
02
STAGE 2
The 5 Methodologies
A deep-dive into each methodology — what it is, how it works in OT,
where it excels, and exactly where it fails. Practical examples throughout.

## Slide 8
STAGE 2 · OVERVIEW
The 5 Methodologies — Fit-for-Purpose in OT Environments
PRIMARY spine
ISA/IEC 62443 Risk Matrix
Purpose-built for IACS. Produces SL-T. Zone/conduit model. Use on EVERY assessment.
PHYSICAL consequence
HAZOP / LOPA
Process safety tool. Reveals what cyber deviations cause physically. Lead on SIS/DCS/safety systems.
ADVERSARIAL threats
STRIDE
Threat modelling for software. Lead on TOS, SCADA, AGV navigation, APIs, external connections.
COMMUNICATION
Bow-Tie Analysis
Bridges cyber and physical safety. Best for executive and HSE audiences. Not a scoring tool.
BRIDGING method
NIST SP 800-30/82
Best when IT risk programme exists in NIST. SP 800-82 adapts for ICS. No SL-T output.
ALWAYS HYBRID
No single methodology covers all three OT risk domains. IEC 62443 matrix is the spine — supplemented by HAZOP for physical consequence and STRIDE for adversarial software threats.
§4.2.3.1 SHALL: Select and document a particular methodology — including the rationale for selection. Hybrid approaches must be fully documented.

## Slide 9
STAGE 2 · METHOD 1
ISA/IEC 62443 Risk Matrix — The Primary OT Cyber Risk Method
Why it is the primary method
• Purpose-built for IACS environments
• Zone + conduit model native to OT network design
• Produces SL-T — the mandatory output for IEC 62443-2-1 CSMS
• Handles adversarial cyber threats, not just accidental failure
• Accepted by regulators, insurers, and safety bodies
• Scalable: can assess 50+ IACS systems consistently
Where it falls short
• Does not deeply analyse the physical consequence chain
→ You need HAZOP to understand what 'hoist manipulation' causes physically
• SL-T determination becomes subjective without rigorous threat input
→ STRIDE provides the adversarial threat detail that sharpens SL-T scoring
The Risk Scoring Framework
L\C
Negligible (1)
Marginal (2)
Critical (3)
Catastrophic (4)
High (4)
HIGH 4
HIGH 8
CRIT 12
CRIT 16
Medium (3)
LOW 3
MED 6
HIGH 9
CRIT 12
Low (2)
LOW 2
LOW 4
MED 6
HIGH 8
Remote (1)
LOW 1
LOW 2
LOW 3
MED 4
LOW
MEDIUM
HIGH
CRITICAL
Risk Score = Likelihood (1–4) × Consequence (1–4). Score ≥ 9 = HIGH. Score ≥ 9 with Catastrophic consequence = CRITICAL requiring SL-T 3.

## Slide 10
STAGE 2 · WORKED EXAMPLE
Practical: IEC 62443 Risk Matrix — Sunrise Refinery SCADA Historian
Asset: SCADA Historian accessible from corporate DMZ without authentication — assess the cyber risk step by step
1
Define the zone
Historian sits in Supervisory Zone (Level 3). Connects to corporate DMZ (external) AND to DCS historian feed (Level 2). This creates a conduit between zones — both must be assessed.
2
Score Likelihood
Threat capability: 3/4 | Attack motivation: 3/4 | Vulnerability exposure: 4/4 (no auth, DMZ-connected)
→ LIKELIHOOD = 3 (Medium) — realistic threat with high exposure, requires some effort.
3
Score Consequence
Direct historian: 2/4 (data manipulation) | Production loss: 3/4 | Lateral pivot to DCS: 4/4 (CATASTROPHIC)
→ CONSEQUENCE = 3 (Critical) — historian provides lateral movement path to DCS.
4
Risk Level + SL-T
Score = Likelihood 3 × Consequence 3 = 9 → HIGH RISK
SL-T 2 assigned to Historian zone. Countermeasures: authentication required, firewall-enforced, audit logging.
SCORE 9 → HIGH RISK → SL-T 2
The historian is HIGH (not CRITICAL) because its own consequence is moderate — but the PIVOT risk to the DCS elevates the score. Always consider lateral movement in risk scoring.

## Slide 11
STAGE 2 · METHOD 2
HAZOP / LOPA — The Physical Consequence Engine
Hazard and Operability Study: applies guide words to process parameters to reveal what deviations cause physically
Where HAZOP excels in OT
• Reveals the physical mechanism of harm from cyber deviations
• Integrates with existing process safety documentation
• Required for SIL verification under IEC 61511
• Familiar to operations and safety engineers who implement controls
• Provides consequence input that sharpens IEC 62443 risk scores
Why HAZOP cannot be the primary cyber method
• Assumes ACCIDENTAL failure — not adversarial intent
• Cannot identify cyber attack paths
• Meaningless applied to software (TOS, historian, SCADA APIs)
• Does not produce SL-T outputs
• Resource-intensive: full HAZOP of large terminal = months
The HAZOP Guide Words Applied to DCS Pressure Controller:
Guide Word
Deviation
Cyber Cause
Consequence
Severity
NO
No pressure signal
Sensor failure / Attacker cuts signal
Controller thinks safe → no response → real overpressure builds
CATASTROPHIC
MORE
Higher reading than actual
Signal manipulation in DCS
Controller reduces feed → process starved → shutdown
MARGINAL
LESS
Lower reading than actual
Attacker spoofs low pressure
Controller increases feed → true overpressure → vessel failure
CATASTROPHIC
REVERSE
Signal direction inverted
Firmware manipulation
Completely wrong control response
CRITICAL
HAZOP tells you WHAT the physical consequence is. IEC 62443 matrix then SCORES it. Without HAZOP, consequence scores on safety-critical systems are systematically underestimated.

## Slide 12
STAGE 2 · METHOD 3
STRIDE Threat Modelling — Adversarial Threats on Software-Intensive IACS
Spoofing · Tampering · Repudiation · Information Disclosure · Denial of Service · Elevation of Privilege
Where STRIDE excels in OT
• Systematically enumerates ALL adversarial attack paths
• Built for software-intensive systems: TOS, SCADA, AGV navigation, APIs
• Captures V2X communication threats (port terminals, autonomous systems)
• Handles supply chain and IT/OT boundary threats natively
STRIDE alone is not enough
• Generates 100–200+ threats for a complex system — no inherent prioritisation
• Does not quantify risk — needs IEC 62443 matrix to score findings
• Does not address physical consequence chains
• Requires software architecture knowledge to execute properly
STRIDE Applied: IGV Navigation System at DP World Terminal
STRIDE
Attack Scenario
Weakness
Consequence
Score
Risk
S · Spoofing
Rogue V2X beacon broadcasts false position
No auth on V2X beacons
IGV routes into pedestrian area / off dock edge
L=3 C=4
CRITICAL
T · Tampering
MITM on Wi-Fi injects false 'obstacle clear'
Unencrypted V2X, no integrity
IGV ignores real obstacle → collision with worker
L=2 C=4
HIGH
D · Denial of Service
Wi-Fi deauth floods all IGV beacons
Standard Wi-Fi vulnerability
All IGVs emergency-stop → terminal halt
L=4 C=3
CRITICAL
E · Elev. Privilege
Vendor account escalates to fleet control API admin
Default API credentials
Attacker commands vehicles directly — bypasses safety zones
L=3 C=4
CRITICAL
STRIDE is the input engine. IEC 62443 matrix is the scoring engine. Three CRITICAL findings drive SL-T 3 for the entire IGV zone — a significantly higher standard than most port operators currently implement.

## Slide 13
STAGE 2 · METHOD 4
Bow-Tie Analysis — Bridge Between Cyber Risk and Physical Safety
Maps threats → top event → consequences, showing prevention and recovery barriers — the executive communication tool
External attacker via DMZ
Malicious insider — OT engineer
Compromised vendor remote access
Prevention Barriers
✓ DMZ Firewall + IDS
✓ MFA on DCS
⚠ Change Mgmt (partial)
✗ Vendor monitoring MISSING
TOP EVENT
DCS Setpoint
Manipulation
→
→
Vessel overpressure → PSV lift
Loss of containment → fire/explosion
Personnel injury / fatality
Recovery Barriers
✓
SIS/ESD (independent)
✓
Pressure Safety Valve
✓
Alarm response procedure
Gap Identified
Vendor access monitoring is MISSING as a prevention barrier. An attacker using a compromised vendor account has NO prevention control between them and DCS manipulation. This is the Priority 1 finding for the board.
Board Communication Value
Bow-Tie presents: three threats, four prevention barriers (one missing), the top event, and three recovery barriers — on one page. Operations, HSE, and the board can understand it without cyber expertise.
When to use Bow-Tie
Use for: (1) The 3–5 highest-consequence scenarios from your IEC 62443 risk register (2) When presenting risk to HSE or executive audiences (3) When integrating cyber risk into the existing process safety bow-tie portfolio. Do NOT use it as the primary risk identification or scoring tool.
Bow-Tie is the COMMUNICATION tool, not the assessment tool. You need HAZOP and IEC 62443 matrix to populate it with accurate barriers and consequences.

## Slide 14
STAGE 2 · METHOD 5
NIST SP 800-30/82 — The Bridging Method for IT/OT Convergence Zones
When your client already has a NIST programme and needs it to extend into OT — use this alongside IEC 62443, not instead of it
Where NIST 800-82 adds value
• SP 800-82 (ICS Guide) is specifically adapted for SCADA, DCS, and PLC environments
• Best for organisations with existing NIST CSF/RMF programmes extending into OT
• Connects IT and OT risk registers in a common language
• Handles SCADA/historian systems at the IT/OT boundary well
• Supply chain risk management is particularly well addressed
Why it is not OT-primary
• No SL-T output — this is a critical gap against IEC 62443-2-1 CSMS requirements
• Physical and safety consequence analysis weaker than HAZOP
• Less accepted by process safety engineers who implement OT controls
• Requires significant adaptation for real-time IACS timing constraints
• NIST language is unfamiliar to operations and control system engineers
When to Use NIST 800-82:
Manufacturing/Industry 4.0
Client has existing NIST CSF. OT systems are new additions. NIST 800-82 bridges the gap while IEC 62443 matrix produces the SL-T for OT zones.
Critical Infrastructure (US)
CISA guidance references NIST CSF. NIST 800-82 maps to NERC CIP requirements. Use alongside IEC 62443 matrix for the technical SL-T scoring.
IT/OT boundary systems
SCADA historians, data diodes, historians, remote access systems. These sit between IT and OT — NIST 800-82 captures both risk dimensions.
Important
Never use NIST 800-82 INSTEAD of IEC 62443 risk matrix in a CSMS context. Use it as a supplementary lens for IT/OT boundary systems. The SL-T must come from IEC 62443.
NIST 800-82 reference: https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-82r3.pdf

## Slide 15
03
STAGE 3
The Decision Matrix
How to select the right methodology — or combination — for any IACS system you encounter. The scoring framework, industry combinations, and CSMS-RA-001 documentation.

## Slide 16
STAGE 3 · DECISION MATRIX
The Methodology Decision Matrix — Score by System Type
Each methodology scored 1–5 per system type. Bold = recommended primary. Italic = useful supporting. Blank = limited value.
System Type
IEC 62443
HAZOP/LOPA
STRIDE
Bow-Tie
NIST 800
SL-T?
Safety systems (SIS/ESD)
★★★★★
★★★★★
★★
★★★★
★★
YES
★★★★★
★★★★★
YES
DCS / PLC / RTU
★★★★★
★★★★
★★★
★★★
★★★
YES
★★★★★
YES
SCADA / Historian
★★★★★
★★
★★★★★
★★
★★★★
YES
★★★★★
★★★★★
YES
OT network & zones
★★★★★
—
★★★★
★★
★★★★
YES
★★★★★
YES
AGV / IGV / Autonomous
★★★★
★★★★
★★★★★
★★★★
★★
YES
★★★★★
YES
TOS / Software-intensive
★★★★
—
★★★★★
★★
★★★★
YES
★★★★★
YES
Physical / HSE consequence
★★★
★★★★★
★★
★★★★★
★★
YES
★★★★★
★★★★★
YES
Vendor / Supply chain
★★★
—
★★★★
★★
★★★★
YES
YES
Executive communication
★★★★
★★
★★
★★★★★
★★★
—
★★★★★
—
★★★★★ = Primary recommendation | ★★★★ = Strong supporting | ★★★ = Useful supplement | ★★ = Limited | — = Not applicable
Document your methodology selection in CSMS-RA-001 with reference to this matrix. The rationale for each selection must be recorded per §4.2.3.1 (SHALL).

## Slide 17
STAGE 3 · INDUSTRY COMBINATIONS
Recommended Hybrid Combinations by Industry Sector
Automated Port Terminal
RTG, IGV/AGV, ASC, TOS — DP World type
PRIMARY:
IEC 62443 Risk Matrix
SUPPORTING:
STRIDE (TOS + IGV navigation + V2X communications)
VALIDATE:
HAZOP (RTG/ASC machinery control)
COMMS:
Bow-Tie (IGV collision and TOS manipulation scenarios)
Refinery / Chemical Plant
DCS, SIS/ESD, SCADA, PLC — process industries
PRIMARY:
IEC 62443 Risk Matrix
SUPPORTING:
HAZOP + LOPA (SIS and safety control loops)
VALIDATE:
LOPA (validate protection layer adequacy)
COMMS:
Bow-Tie (loss-of-containment and ESD defeat scenarios)
Water & Wastewater
SCADA, PLC dosing systems, pumping stations
PRIMARY:
IEC 62443 Risk Matrix
SUPPORTING:
HAZOP (chemical dosing control systems)
VALIDATE:
—
COMMS:
Bow-Tie (public health contamination scenario)
Power Generation
EMS, SCADA, turbine control, protection relays
PRIMARY:
IEC 62443 Risk Matrix
SUPPORTING:
STRIDE (EMS/SCADA + external grid connections)
VALIDATE:
HAZOP (turbine and generator control systems)
COMMS:
Bow-Tie (grid stability and blackout scenarios)
Copy the rationale text from your chosen combination directly into CSMS-RA-001 Section 4 (Selected Methodology) — adapting for your specific site and systems.

## Slide 18
04
STAGE 4
Worked Examples
Two complete end-to-end assessments. Watch the methodology selection, risk scoring, and countermeasure derivation from start to finish.

## Slide 19
STAGE 4 · EXAMPLE 1
Case Study: LAN-Connected Triconex SIS — Sunrise Refinery
Discovery: Unit 3 SIS reachable from corporate ERP VLAN with no firewall between them
🚨 The Discovery
Network mapping (CSMS-RA-003) reveals that the Unit 3 Triconex SIS — which controls emergency shutdown for Unit 3 — has an Ethernet port on the same VLAN as the corporate ERP. No firewall. Anyone on corporate can reach the SIS.
1
Methodology Selection (CSMS-RA-001)
Decision matrix: SIS = IEC 62443 primary + HAZOP supporting + Bow-Tie for executive communication.
Justification: SIS is safety-critical (IEC 61511 SIL 2). HAZOP required for physical consequence chain. IEC 62443 produces SL-T. Bow-Tie for board presentation.
2
HAZOP — Physical Consequence Identification
NO interlock signal when high pressure: Vessel overpressure → explosion/BLEVE → CATASTROPHIC
SPURIOUS shutdown triggered: Uncontrolled Unit 3 cool-down → product solidification → days offline → CRITICAL
Cause-and-effect matrix altered: Wrong equipment responds → hidden hazard builds → CATASTROPHIC
3
IEC 62443 Scoring (CSMS-RA-007)
R-SIS-001: External attacker disables ESD via corporate LAN | L=4, C=4 | Score 16 | CRITICAL | SL-T 3
R-SIS-002: Insider triggers false ESD via SIS workstation | L=3, C=3 | Score 9 | HIGH | SL-T 2
R-SIS-003: Vendor remote access used to alter cause-and-effect | L=3, C=4 | Score 12 | CRITICAL | SL-T 3
4
Countermeasures (SL-T 3 Required)
IMMEDIATE (24hr): Physically disconnect SIS from corporate VLAN. Suspend all vendor accounts with SIS access.
WITHIN 30 DAYS: Deploy unidirectional gateway/data diode. Implement MFA on all SIS access. Vendor access: supervised only, time-limited, logged.
Score 16 = Maximum on the 4×4 matrix. This is an immediate shutdown of the vulnerability before the detailed assessment completes. §4.2.3.13: document everything.

## Slide 20
STAGE 4 · EXAMPLE 2
Case Study: IGV Navigation — Automated Port Terminal
DP World-type terminal · IGVs use GPS + V2X + fleet management API connected to TOS
The Scenario
IGVs navigate using GPS positioning and V2X beacons from fixed infrastructure. Fleet management server connects to TOS via REST API. Vendor has remote access to fleet management for maintenance.
Question: What are the CRITICAL cyber risks and what SL-T does the IGV zone require?
Step 1: Methodology Selection
PRIMARY
STRIDE (IGV nav + V2X + fleet API)
SUPPORTING
IEC 62443 Matrix (zone scoring)
VALIDATE
Bow-Tie (IGV collision scenario)
Why STRIDE leads: IGV threats are adversarial and software-focused — V2X spoofing, positioning data manipulation, API privilege escalation. HAZOP would miss the entire V2X attack surface.
Step 2: STRIDE Output → IEC 62443 Scores
R-IGV-001
L4×C4=16
CRITICAL
Spoofing — Rogue V2X beacon
SL-T 3
R-IGV-002
L2×C4=8
HIGH
Tampering — MITM obstacle data
SL-T 2
R-IGV-003
L4×C3=12
CRITICAL
DoS — Wi-Fi deauth fleet halt
SL-T 3
R-IGV-004
L3×C4=12
CRITICAL
EoP — Vendor API escalation
SL-T 3
Key Finding
Three CRITICAL risks → SL-T 3 for the entire IGV zone. Most port operators currently implement SL-T 1. This gap requires urgent countermeasure programme.
STRIDE produces the findings. IEC 62443 matrix scores them. Bow-Tie communicates the 'IGV collision due to V2X spoofing' scenario to the board with barrier gaps clearly visible.

## Slide 21
05
STAGE 5
Application & Mastery
The seven principles of OT risk assessment. The complete CSMS-RA-001 checklist. The mindset shift from IT risk professional to OT assessment practitioner.

## Slide 22
STAGE 5 · MASTERY
The 7 Principles of OT Risk Assessment Mastery
1
Start with physical consequence
Ask: what is the worst physical thing that can happen here? Work backwards to cyber causes. Not vulnerability → impact.
2
Never use a single methodology
IEC 62443 matrix is your spine. Add HAZOP for physical consequence. Add STRIDE for software attack paths. Always hybrid.
3
SL-T is mandatory — everything else supplements
The CSMS requires SL-T to drive countermeasures. HAZOP and STRIDE feed into IEC 62443 matrix — which produces SL-T.
4
Security controls must not create safety hazards
Every control must be checked for HSE impact. §4.2.3.11 (SHALL) — integration is mandatory, not optional.
5
Follow the Annex B sequence — always
High-level first. Business rationale before technical work. Detailed findings without risk narrative = ignored reports.
6
Document the methodology selection (CSMS-RA-001)
§4.2.3.1 (SHALL). Show alternatives evaluated and the specific reasons for selection. This is the first document an auditor requests.
7
The risk register is a living document
§4.2.3.10 (SHALL): Reassessment triggers must be documented. Every system change triggers a risk register review.
Mastery is not knowing the methodology names. It is knowing when to use them, how to combine them, and how to justify the combination to an auditor or regulator.

## Slide 23
STAGE 5 · CSMS-RA-001
CSMS-RA-001 Methodology Selection — The Audit Checklist
Before submitting your methodology selection record, every item below must be confirmable. These are the questions an IEC 62443 auditor will ask first.
☐
The selected methodology is named and documented in CSMS-RA-001
§4.2.3.1 SHALL
☐
At least two methodologies were evaluated before selection (alternatives documented)
§4.2.3.1 SHALL
☐
The rationale for selection explains why this method fits THIS environment
§4.2.3.1 SHALL
☐
The method produces SL-T — or explicitly shows how SL-T is derived from its outputs
CSMS requirement
☐
Physical consequence analysis is included for any safety-critical system in scope
§4.2.3.11 SHALL
☐
STRIDE analysis is included for software-intensive or externally-connected systems
Best practice
☐
The selection has been endorsed by both OT Security Lead AND HSE representative
Governance
☐
Training records exist for all assessment participants on the selected methodology
§4.2.3.2 SHOULD
☐
Reassessment triggers are documented in CSMS-RA-009
§4.2.3.10 SHALL
☐
Methodology review schedule is established (maximum 3 years)
Best practice
Remember
An undocumented methodology selection is a SHALL non-conformance against §4.2.3.1. It is the first document an auditor or regulator will request.
Template: CSMS-RA-001_Methodology_Selection.docx — available in the OpenCSMS GitHub repository.

## Slide 24
STAGE 5 · QUICK REFERENCE
Quick Reference: Methodology Selection at a Glance
Assessing...
Lead with...
Add...
Validate with...
Safety-critical (SIS/ESD)
IEC 62443 Matrix
HAZOP + LOPA
Bow-Tie
IEC 62443 Matrix
DCS / PLC (process)
IEC 62443 Matrix
HAZOP
Bow-Tie for key scenarios
IEC 62443 Matrix
SCADA / Historian
IEC 62443 Matrix
STRIDE
—
IEC 62443 Matrix
OT network / zones
IEC 62443 Matrix
—
—
IEC 62443 Matrix
AGV / IGV / autonomous
STRIDE
IEC 62443 Matrix
Bow-Tie (collision)
STRIDE
TOS / software-intensive
STRIDE
IEC 62443 Matrix
—
STRIDE
Physical / HSE consequence
HAZOP
IEC 62443 Matrix
Bow-Tie
HAZOP
Vendor / supply chain
STRIDE
IEC 62443 Matrix
Bow-Tie
STRIDE
Executive communication
Bow-Tie
IEC 62443 (scores)
—
Bow-Tie
The Core Rule
IEC 62443 Risk Matrix appears in EVERY combination because it is the only method that produces SL-T. It is always the spine, even when STRIDE or HAZOP leads the threat/consequence identification.
IEC 62443-2-1:2010 — Risk Assessment Methodology Training · OpenCSMS Open Source CSMS Project

## Slide 25
The Mindset Shift
From IT risk professional to OT assessment practitioner
IT Risk Mindset
OT Risk Mindset
Start with vulnerabilities (scan, find CVEs)
→
Start with physical consequence, work backwards
Worst case = data breach, regulatory fine
→
Worst case = fatality, environmental release
Apply controls from ISO 27001 Annex A
→
Validate every control against HSE impact first
Availability is secondary to confidentiality
→
Availability is primary — often before confidentiality
Single methodology (ISO 27005, FAIR, OCTAVE)
→
Hybrid always: IEC 62443 + HAZOP + STRIDE
Patch immediately on schedule
→
Patch after vendor approval, change management, staging test
Risk register reviewed annually
→
Risk register updated on every change, every trigger event
"Irrespective of the quality of a CSMS, if it is not used, it does not add any value to the organisation and does not help reduce risk."
IEC 62443-2-1:2010 §4.4.2 Rationale